## Sheet1
Design, Supply, Installation, Testing, and Commissioning of 12MWp Solar PV Power Plant with 36MWh of Battery Energy Storage System Including a 13.5km of 33kV Evacuation line for BEC Berbera, Somaliland. Reference No.: SO-MOEM-445076-CW-RFB
S.N. | Volume/Section | Clause No. | Bidder's Query | Employer's Clarification
1 | Section II – Bid Data Sheet (BDS) | ITB 11.2 (i) Documentary evidence confirming that the Manufacturers’ is Tier 1 with at least a minimum 10 years’ experience of manufacturing similar equipment. Documentary evidence shall include information of the factory locations. | We understand that the Tier 1 refers to the Energy Storage and Solar Module Maker Tier 1 List issued by BloombergNEF, Please confirm. If our understanding is correct, we need to remind you that only solar module and energy storage have this Tier 1 list. | Manufacturers for BESS and Solar Modules shall be of Tier 1 and shall be shown in the quartely issued Bloomberg NEF editions.
2 | Section III – Evaluation and Qualification Criteria | 3. Evaluation of Financial Part (i) Economic Factor: O&M Cost (US$) is the value of the O&M contract - 2% of the CAPEX shall be used until the year 25 | We understand that 25 years of operation and maintenance work is not within the scope of this project. Please clarify what the O&M Cost (US$) refer to here? | Ist is the estimated projected O&M cost for the plant over its operational period.
3 | VOLUME II. EMPLOYER’S REQUIREMENTS | 3.0 PROJECT SPECIFIC DATA Project Coordinates：10.3166342, 44.9495721 | Please provide accurate boundary coordinates and occupation drawings for the Solar PV Power Plant | Refer to the site assessment report for boundary coordinates and occupation drawings
4 | VOLUME II. EMPLOYER’S REQUIREMENTS | 13.5 KM 33kV Evacuation line of OH Line circuit and an underground circuit complete with poles, conductors, insulators as per relevant standards. The 33kV evacuation line off takes power from the new PV power plant to the newly proposed Distribution substation | Please provide the route diagram of the 13.5 KM 33kV Evacuation line | Refer to the route diagram of the 13.5 km 33 kV Evacuation line
5 | VOLUME II. EMPLOYER’S REQUIREMENTS | The newly proposed Distribution Substation comprising of 2No. 5/6.5MVA ONAN/ONAF of 33/11 kV ONAN type transformers complete with all its necessary protection schemes. | Please provide detailed boundary coordinates and land occupation drawings for the proposed Distribution Substation | Refer to the site assessment report for boundary coordinates and occupation drawings
6 | Section II & II, Vol. 1 | Section II BDS Subclause 11.2(i) The Bidder shall submit the following additional documents: Bidder's audited Financial Statements for the last eight (8) years as stipulated in Section II of the Evaluation criteria. Section III EQC Subclause 3.1 Financial Capacities Submission of audited balance sheets or if not required by the law of the Bidder's Country, other financial statements acceptable to the Employer, for the last five (5) years (2019-2023) to demonstrate the current soundness of the Bidders financial position and its prospective long-term profitability. | The two clauses conflict with each other. Please clarify how many years' Financial Statements shall be submitted by the Bidder. | Required audited accounts are from 2019-2023.Biders are urged to submit their certified Audited accounts over the stipulated period
7 | Section II BDS, Vol.1 & Vol.2 | ITB 11.2(i) The Bidder shall submit the following additional documents:- -Spare Parts - Recommended list of tools and Spares to be supplied with PV Panels, Inverters, BESS, SCADA, Medium Voltage Switchgears, Transformers and Cables for three year's preventive maintenance consumption after the 12 months Defects Liability period. 3.0 PROJECT SPECIFIC DATA 3.1 Scope of Design and Supply of Plant and Installation Services 3.1.1 Solar PV Power Plant General Scope The project scope in this bid includes the design, supply, installation, configuration, testing and commissioning of a Solar Power Generating Plant with its associated Battery Energy Storage Services. The project defect liability period is Eighteenth (18) Months starting from the date of Operational Acceptance Certificate. | The two clauses conflict with each other. Please clarify the exact period of Defects Liability. | Defect liability defect liability period for the project is 12 month from the Date of Operational acceptance of the plant as indicated under clause 27.2 of the proposed contract.
8 | RFB BEC -Volume-II | 4.9.3 System AC-DC-AC Efficiency | The AC side here refers to the 0.8kV output side of PCS, the cabinet transformer medium voltage side or the 33kV connection point | RTE is measured at The Point of Connection (POC) which is 33kV of the common bus
9 | RFB BEC -Volume-I | Functional Guarantees of the facility | 1.The peak DC power of the photovoltaic system is in the unit of MWp. After passing through the inverter, it should be the AC power in the unit of MW, and the unit of the AC power should not be MWp. | 12MWp is the DC capacity while 10.26MW is the converted AC capacity
10 |  |  | 2.Is the required AC output power of the photovoltaic power generation for this project 10.26 MW or 14 MW? | 12MWp is the propoed DC capacity of the project while 10.26 is the AC capacity
11 |  |  | 3.During the beginning of life (BOL) operation stage of the energy storage system, is the charge-discharge round-trip efficiency evaluated according to 90% or 95%? Where is the test point (POC point) for this cycle efficiency? Please indicate it in the following figure: A/B/C/D/E? According to the requirements of the IEC62933-2-1 standard, the POC point should be point E. | 33KV is the POC Point for the RTE measurement
12 |  | BESS System AC-DC-ACEfficiency ＞90% | Does 90% efficiency include auxiliary load consumption within the energy storage system? | Auxiliary loads are also fed from the same common bus. 90% is inclusive of all
13 |  |  | According to the requirements of the IEC62933-2-1 standard, it is necessary to conduct metering in the 33kV switchgear of the booster station, including the consumption of the auxiliary power supply within the energy storage system. Currently, no manufacturer can achieve the RTE = 90% charge-discharge round-trip efficiency required by this project. Will bids with an efficiency lower than 90% be accepted and evaluated according to the promised values of the bidders? | The bidder shall stick to the requirement by ensuring to fully comply with the employer's requirement
14 |  |  | 1.This project is a 12 - MWp/10.26 - MWac photovoltaic power generation project, equipped with a 9 - MWac/36 - MWh energy storage system. The AC power of the photovoltaic power generation is almost the same as that of the BESS. The 4 - hour energy storage charging time will lead to 80% of the photovoltaic power being used to charge the BESS. Due to the power loss during the charging and discharging of the BESS, it is expected that 15% of the photovoltaic power will be wasted. Please provide how to coordinate and control the photovoltaic power generation and the energy storage charging and discharging, and evaluate whether the bidding requirements are reasonable. | A smart control system should monitor real-time generation and storage, dynamically adjusting power flow between the PV system, BESS, and the grid. Its is the bidder's resposnsibility to design power plant that could achieve the projected output power as stipulated in the employer's requirement
15 |  |  | 2.According to the above content, the tenderer needs to confirm with the power grid company about the maximum AC power output from this project to the power grid side. Only in this way can we use the PVSYST software to conduct the simulation of "PV + BESS peak - shaving and valley - filling". Without limiting the grid - connected power value, the energy storage in the simulation report will not charge/discharge | Bidder's are required to do proper mathermatical oriented design to come up with an efficient fool proof design. Simulation aren't admissible as a design but can accompany the design as a value addition.
16 |  |  | According to the requirements of the IEC61724 standard, Tmod is the annual average temperature of the photovoltaic modules. However, the bidding requirement is to conduct the assessment and calculation based on the monthly average temperature of the photovoltaic modules. Should it be implemented in accordance with the IEC61724 standard? | Follow the bidding requirement and conduct the assessment using the monthly average temperature, as the project site experiences extreme seasonal fluctuations. The IEC 61724 standard avoids such variations by using annual averages, which may not reflect the specific conditions of your site
17 |  |  | 1.Please clarify where the assessment points for the photovoltaic power generation and the 90% power generation efficiency are. Is it at the 33kV switchgear in the booster station or at the AC output side of the photovoltaic inverter? 2.If the assessment of the 90% photovoltaic power generation efficiency is carried out at the 33kV switchgear in the booster station, there is currently no actual completed project that can achieve this. Will bids with an efficiency lower than 90% be accepted and evaluated according to the promised values of the bidders? | Its is at the 33kV POC of the power plant
18 | RFB BEC -Volume-II |  | The bidding documents mention the combiner box and the string - type inverter. At present, the centralized inverter scheme is "combiner box + integrated inverter - step - up equipment", and the string - type inverter scheme is "string - type inverter + box - type transformer". Please clarify whether the centralized inverter scheme or the string - type inverter scheme is adopted for this project? | The use of central Inverter isn't permitted. Only String inverter is allowed for the project provided the speicifed rating capacity can be met.
19 |  |  | In the energy storage PCS step - up container and photovoltaic medium - voltage container, CCV - type ring - main unit (RMU) is configured. Consultation: For the equipment of Siemens/ABB/Schneider, the maximum complete set of equipment they can provide for "short - circuit current/rated duration" is "25kA/3S". There is no SF6 medium - voltage equipment of 31.5kA/3S for new energy containers. Is the Chinese - brand 33kV ring - main unit acceptable? | The bidder shall stick to the required short circuit withstand capability as required in the bid
20 |  | Lightning mast/conductor, placed at strategic locations, shall be used to protect the arrays against lightning protection. The bidder shall give a detailed design showing the location of the lightning conductor/masts and the protection coverage on the array without causing any shadow on the modules to the Employer. | The bidding requires the construction of lightning rods in the photovoltaic plant area, and the lightning rods should not cast shadows on the photovoltaic array. Please clarify the date and time range during which there should be no shadow occlusion. It is not acceptable to conduct the assessment based on no occlusion throughout the year/24 hours a day, as this would make it impossible to construct the photovoltaic array. | The assessment for shadow occlusion should focus on the peak sun hours, typically between 09:00 AM and 4:00 PM
21 |  | Availability of the BESS based on projected scheduled outage hours and projected unscheduled outage hours shall be at least equal to or greater than 95% on an annual basis. | The availability of the energy storage system (BESS) must meet the 95% requirement under both planned and unplanned conditions. This is unreasonable because if there are too many power outages in the power grid, the 95% availability may also be affected. It is unreasonable to assess the contractor in such a situation. Is it acceptable that the availability of the contractor's equipment quality is not less than 95%? | The contractor's equipment quality and operational reliability should be assessed to ensure its availability remains at least 95% under normal conditions, excluding any external grid-related issues
22 |  | The enclosure material shall be 6mm, 3CR12 or stainless steel. | A thickness of 6mm is usually the requirement for marine - transport containers. In China, manufacturers of battery - container shells can only provide galvanized steel plates with a thickness of 2mm, and the compartments are filled with 20mm - thick refractory materials, which can achieve a fire - resistance time of 2 hours and meet the requirements of NFPA 855. Please clarify: Is a container - shell steel - plate thickness of 2mm acceptable? | The bidder shall stick to the requirement in the bid
23 |  | In the case of string Inverters, average voltage drops (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. | Regarding the calculation of the influence of cable operating temperature on cable resistance, the requirement of 0.5% average voltage drop for DC cables is too high. Currently, it is impossible to truly achieve this requirement in global implementation projects. Is it acceptable to adopt the common voltage drop requirements of 1.5% or 1% in current global projects? | as specified under Section 4.4.1 Warranty, for string inverters, the average voltage drops (from PV module to string inverter) must be limited to 0.5% of the rated voltage drop. Achieving a 0.5% voltage drop is feasible. The bidder shall stick to the requirement in the bid
24 |  | PV module Front glass coating: ≥ 3.2mm anti reflect coating | The thickness of the front glass of the photovoltaic module is 3.2mm, which is the requirement for single - side - power - generation modules. Is it acceptable to use double - side - power - generation modules with a front glass thickness of 2.0mm + a rear glass thickness of 2.0mm? | The recent produced bifacial modules with lesser coating thickness could be considered provided that they meet the bid requirment
25 |  | The Mounting Structure shall be Fixed-tilt type Azimuth 0º true South/north as per the project location. Tilt angle shall ensure that there no imposing shadow from the arrays. | Please clarify the dates and time periods during which there should be no shading between the photovoltaic arrays, for example: December 21st, from 9:00 to 15:00. | PV plant shall be designed in a manner that there is no imposed shades through out the day regardless of timing.
26 |  | The Photovoltaic PV module shall consist of Silicon mono (Mono PERC) Photovoltaic modules of capacity rated at STC. T | PERC - type photovoltaic modules have gradually withdrawn from the market. Is it acceptable to use N - type TOPcon photovoltaic modules, which have higher efficiency and less attenuation? | Yes, it is acceptable to use N-type TOPCon photovoltaic modules, as they offer higher efficiency compared to PERC-type modules on a condition that they meet the required technical specifications and performance standards for the project.
27 |  | 14.2.5Trial operation tests After passing the above tests, the trial operation period shall be conducted. Successful Trial Operation will be deemed achieved when the system has first achieved and maintained an average Availability of 97% for a minimum of 168 consecutive hours without the need for any on-site presence excluding external faults. | Is 97% availability only the requirement for the "Trial operation tests" stage? | Yes, 97% availability is the requirement for the 'Trial Operation Tests' stage only. However, prior to this trial test, various other tests, including grid code compliance tests as per IEC 62933-2, are required to verify the system's performance in terms of energy capacity, power rating, round-trip efficiency, system response, and other factors
28 |  |  | There is a conflict in the availability requirements of this project, which are 98% and 95% respectively. Please clarify the availability assessment criteria for the photovoltaic power generation and energy storage systems respectively. | The photovoltaic power generation system requires a minimum availability of 98%, while the energy storage system (BESS) requires a minimum availability of 95%, accounting for both planned and unscheduled maintenance. Availability is calculated based on the system's power capability at the Point of Connection (POC) and downtime due to maintenance
29 |  | Minimum 36 MWh Nameplate capacity with at least 34MWh dispatchable at the beginning of life and not less than 70% of this capacity at any point of time up to End of Battery Life. | Is 34 MWh the AC discharge capacity on the 33 - kV side? Does it include the power consumption of the internal auxiliary loads in the energy storage system? | 34 MWh refers to the dispatchable capacity of the energy storage system at the beginning of its life, representing the energy available for discharge at the AC discharge capacity on the 33 kV side. This value is included since auxiliary loads are laso fed from the POC 33kV Bus
30 |  | Minimum 36 MWh Nameplate capacity with at least 34MWh dispatchable at the beginning of life and not less than 70% of this capacity at any point of time up to End of Battery Life. | Is 36 MWh the minimum DC nameplate capacity of the battery? There is no need to consider the discharge losses of DC and AC. | Yes, It’s the nominal rating of the BESS system
31 | RFB BEC -Volume-II | 15. APPENDICES APPENDIX 1: SLD FOR THE POWER PLANT... To be Inserted | Please provide the SLD and Electrical general layout of the substation. | Refer to the SLD Diagram
32 | RFB BEC -Volume-II | 4.8.6 Detailed Technical Requirements for GIS Components GTP FOR 33kV GISCOMBINER PANEL | Regarding the Rated short-circuit breaking current fo the 33kV system, the GTP shows 31.5kA/3s, but the bidding document shows 40kA rms 3 sec for bus coupler/incomer and 31.5kA for bay module, please determine the Rated short-circuit breaking current of the 33kV GIS. | 40kA is for coupler bus while 31.5kA is for the bay feeders.
33 | RFB BEC -Volume-II |  | Please provide the GTP of the auxiliary transformer for the 33/11kV substation. | The required auxiliary transformer is 50 kVA, and the bidder is required to submit the (GTP) for the transformer as part of their bid submission
34 | RFB BEC -Volume-II |  | According to the description in the bidding document, 33/11kV transformer is required for this project, but the 11kV system is not mentioned in the bidding document. Please make it clear whether the 11kV equipment is included in the scope of this bidding. If it is included, please provide the GTP of the 11kV equipment for the 33/11kV substation. | The project scope ends at the Transformer point of connection. Downstream distribution isn't in the current scope
35 | Volume-II |  | Please clarify whether the automatic reclosing device must be configured independently or can it be integrated within the protection relay? | Shall be integrated with all reclosing relays and portection features shall be coordinated with the overall protection schceme of the project
36 |  |  | Please clarify whether the battery is of lead-acid or Nickel Cadmium type. Are there any requirements regarding the capacity of the battery? | The required battery is an LFP (Lithium Iron Phosphate) type, designed for site-specific climatic conditions. It must provide 6000 cycles at rated capacity, with a 95% Depth of Discharge (DoD), at 25°C and a 0.25 C Rate of Discharge.
37 |  |  | Please clarify whether the 33kV protection and control device can be installed locally within the switchgear cabinet. | The 33 kV protection and control devices Shall be incorporated within the GIS 33kV Panel
38 | Volume-II |  | No 48V DC charger and battery is required in bids. The 48V DC power supply will be DC/DC converter configured with 110V DC chargers. No 48V battery will be supplied. Kindly confirm it. | As mentioned in the bid document, no 48V battery will be supplied. Instead, the 48V DC power supply is required it will be generated using a DC/DC converter that is configured with 110V DC chargers
39 |  |  | No communication equipment such as SDH/MPLS-TP and PABX is required in bids. Kindly confirm it. If the communication equipment is in the work scope, please specify the requirement. | All SCADA and EMS shall be designed fully including all necessary communication devices that can make the system functional
40 | RFB BEC -Volume-II | 3.1.1 Solar PV Power Plant General Scope | In 3.1.1, it is mentioned that the wind speed is 11.88m/s, is this wind speed a 10min average wind speed with an annual probability of occurrence of 0.02? Or please provide the basic wind speed used for the design of PV mounts. | please refer to the site assessment report
41 | RFB BEC -Volume-II | 3.1.1 Solar PV Power Plant General Scope | Please provide a topographic map of the site。 | please refer to the site assessment report and the EIA Report
42 |  |  | Please provide geological survey documents for the project (including foundation bearing capacity, soil corrosivity, seismic intensity conditions, etc.) | please refer to the site assessment report and the EIA Report
43 |  |  | Please provide the atmospheric corrosion condition for the project. | please refer to the site assessment report and the EIA Report
44 | RFB BEC -Volume-II | The number and size of new buildings for this project could not be found | Please specify the number and scale of new buildings required for this project | This shall be designed in coordination with the contractor at the execution stage
45 | Volume-II |  | Please clarify whether an outdoor fire hydrant system (including fire pump room, fire water tank, fire water pump and pipeline, outdoor fire hydrant) is required within the station area? | it’s the responsibility of the bidder to design power plant that is properly protected in line with the laid down standards and that of NFPA. Use employer's requirement as a guide line for coming with such design
46 | Volume-II |  | Please clarify the sources of domestic and fire-fighting water (such as drilling wells for water, transporting water outside the station, or supplying water through municipal pipelines) | The employer will provide water harvesting and storage, while the contractor is responsible for sourcing and managing all other water needs during project implementation | A3SW
47 | RFB BEC -Volume-II | 10. OVERHEAD LINES & ITS ACCESSORIES | Please clarify the width of the corridor clearing for the installation of the 33kV overhead transmission line. | Refer to the employer's requiremenent for such details about clearance
48 | RFB BEC -Volume-II | 10.10 Line Supports and Foundations | Please clarify the design standards for the foundation dimensions of the concrete poles for the 33kV overhead line section. Is it based on the NF-C11-201 standard or another standard | The concrete poles for the 33kV overhead line must be designed and manufactured according to the TSP/03/05 series standards, or equivalent or superior standards. These standards will define both the foundation dimensions and the design and material specifications for the poles. If NF-C11-201 or other local standards are referenced, they should align with or be integrated into the project-specific standards
49 | RFB BEC -Volume-II | 10.12 Physical and Mechanical Properties of Concrete Poles | Since the RFB BEC - Volume-II: '10.12 Physical and Mechanical Properties of Concrete Poles' mentions that the ultimate load of concrete poles is a maximum of 6kN, please clarify if it is possible to design and install concrete poles with an ultimate load greater than 6kN. | yes it s possible to design to design and install concrete poles with an ultimate load greater than 6kN, as long as they meet with project stnadrad requiements and the applicable design codes and regulations
50 | RFB BEC -Volume-I ‘Section IV - Bidding Forms’ | Schedule of Rates and Prices Schedule No. 1. Plant and Mandatory Spare Parts Supplied from Abroad | Line 24 mentions‘13.5 km 3Phase 33kV OH Line in 195 mm2 ACSR (Wolf) conductors, including, concrete poles, insulators, cross arms, stays, earthing, surges fittings, and any other fittings necessary for proper functioning of the system’ Please provide the KMZ and other related files for the overhead line route of this project | Refer to the route diagram of the 13.5 km 33 kV Evacuation line
51 |  |  | Please provide the BOQ files for the ‘13.5 kM 33kV Evacuation line of OH Line circuit and an underground circuit’ | Refer to the price schedules provided in volume one of the bid document for pricing purposes
52 | RFB BEC -Volume-II | / | Please share the BOQ in Transmission line project. | Refer to the price schedules provided in volume one of the bid document for pricing purposes
53 | RFB BEC -Volume-II | 3.0 PROJECT SPECIFIC DATA ＆ 10.3 Working Conditions | The wind speed in section 3.0 -Table 1 is described as 11.88 m/s. The wind pressure in section 10.3 is described as 400N/㎡. Please confirm the design wind pressure of transmission line project. | Refer to the site assessment and the EIA reports
54 | RFB BEC -Volume-II | / | Please confirm the wind span of transmission line project. | Refer to the site assessment and the EIA reports
55 |  |  | Could you please specify the correct location for the PV plant? Should it be on side 1 or side 2? Kindly share with us the land corner coordinates. | Refer to the provided route diagram of the plant
56 |  |  | Regarding the reference project, Is it mandatory to have at least three (3) completed projects, each with a minimum capacity of 15MWp PV and 9MW/40MWh battery storage.The projects must have been executed within the last ten (10) years and in satisfactory operation for at least six (6) months before the submission date. For each project, Completion Certificates, Award Letters, signed contracts, and summary pages of the final accounts must be submitted, along with the contact details of the relevant personnel ? We have completed projects with capacity as follows: Seychelles – 5MWp PV / 5MWh BESS Jordan – 6.18MWp PV (8MWac) + 1.375MW / 2.752MWh BESS + 15MVA Diesel Generator Chad – Under construction (2.5MW PV / 5.015MWh BESS) | Previous completed projects required capacities remain as it is in the bid
57 |  |  | Please provide us with the single-line diagram file | Refer to the SLD Diagram of the system
58 |  |  | Could you kindly confirm if the project requires a CCTV system on the boundary fence? | CCTV within the site and for securing the material supplied by the contractor shall be catered by the bidder. Permiter wall Serveilanace is in the scope of the ESP
59 |  |  | Can you specify the MV route from the PV plant to the Point of Connection (POC)? | Refer to the route diagram of the system
60 |  |  | What’s the strength grade of the concrete poles already constructed locally in Somaliland? | various grades are constructed and It’s the bidder to find out and do its own research over such
61 |  |  | What's the grade range of the concrete poles in Somaliland?(in the bidding docuemnt, only 250daN and 300daN are mentioned) | It’s the bidder to find out and do its own research over such
62 |  |  | Where is the circuit breaker constructed? Is it integrated together with the 33/11 substation? | Refer to the drawing for the distribution Substation, there is GIS 33kV Panel provided to offer protection to the two transfomers. The panel is complete with all its protection mechanism including breakers
63 |  | Schedule of Rates and Prices Schedule No. 1. Plant and Mandatory Spare Parts Supplied from Abroad | Line 28 mentions‘5.0 /6.5MVA (ONAN/ONAF) 33/11 kV transformer as specified in the tender document ’ .We would like to know for the 33/11kV transformer installation, whether it is installed on the 33kV Evacuation Line poles, distribution room style, or outdoor substation style？ | it is not practical to mount such types of transformers on poles
64 |  |  | There is one 33-kilovolt overhead line and one 33-kilovolt underground cable in the BOQ. Do both lines need to be constructed? | yes both lines needs to be constructed
65 |  |  | What is the construction path direction of the transmission line? Regarding the settlement method of this project, especially for the transmission line part, how should the settlement be conducted when the access point location change causing the path to increase or decrease? | The route is already cleared and known. No resettlement is envisaged
66 |  |  | Is the 13.5km 33kV evacuation line included in the EPC contractor's scope, or is it a separate contract? | it is included in the contractors scope
67 |  |  | Are there any geotechnical or environmental studies available for the site that bidders can access? | For now, refer the breif site assessment report, then at the exucation period there will be geotechnical report avaialbe
68 |  |  | For the 33kV line, if right-of-way issues cause delays, will the Employer assist, or is this solely the contractor's risk? | Refer to the GCC 10.4 and its amendment under PCC 10.4
69 |  |  | What are the exact grid code requirements for interconnection with BECO's network? | It’s the responsbility of the contrcator to coordinate with the local utility service provider over the integration of the two systems
70 |  |  | Please confirm whether the site clearance and Right of Way (ROW) for the 13.5 km transmission lines will be provided by the Employer | ROW has already been cleared.
71 |  |  | Please clarify if the employer is responsible for paying all customs and import duties for the Plant listed in Price Schedule No. 1. | Refer to PCC 14.2 (a) & (b) of the contract
72 |  |  | Are there preferred technology specifications for the BESS (e.g., LFP (LiFePO₄, NMC Lithium ETC? | The required battery is an LFP (Lithium Iron Phosphate) type, designed for site-specific climatic conditions
73 |  |  | Please provide the red - line drawing of the plant site area. | Refer to the SLD
74 |  |  | Please provide the Topographic map and Geological Report of the whole plant. | Refer to the site report, EHS and EIA
75 |  |  | Please provide the General Layout plan of the whole plant, including the New Substation. | Refer to the SLD and the site drawings
76 |  |  | Please provide the Electrical SLD of the whole plant, including the New Substation. | Refer to the SLD
77 |  |  | Please provide the Line route maps of the two outgoing transmission lines. | Refer to the Line route Map
78 | Volume I | Bidder’s audited Financial Statements for the last eight (8) years as stipulated in Section III of the Evaluation criteria. | The requirement for Bidder to submit the financial statement is inconsistent between BDS and Evaluation Criteria, please clarify which requirement shall be followed. | Required audited accounts are from 2019-2023.Biders are urged to submit their certified Audited accounts over the stipulated period
79 | Volume I | Submission of audited balance sheets or if not required by the law of the Bidder’s Country, other financial statements acceptable to the Employer, for the last five (5) years (2019-2023) to demonstrate the current soundness of the Bidders financial position and its prospective long term profitability
80 | Volume I | The bidder should have an experience in Design, Supply, Installations, TestingandCommissioning for the PV Power Plant with an integration of BESS and Diesel Gensets. The bidder shall demonstrate to have carried out at least Three (3No.) projects which are completed with a minimum capacity of 15MWp PV with 9MW/ 40MWhr Battery Storage Capacity each. The projects shall have been carried out in the last ten (10) years and shalhave been in satisfactory operation Six (6) months before the submission date. CompletiorCertificates, Award letters, signed contracts and summary pages of the final accounts shall besubmitted for each together with the details of the contact personnel. | The requirement for Bidder to submit the specific experience is inconsistent between BDS and Evaluation Criteria, please clarify which requirement shall be followed. Meanwhile, the description for Substantial completion is 80% or more Plant and installation completed under the contract in Evaluation criteria. But in BDS, it is required the completed project experience, please please clarify which requirement shall be followed. | The projects should have been completed 6 months prior the closure date of this bid
81 | 65 & 66 | (a) Participation as contractor, joint venture member, or subcontractor, in at least three (3) contracts within the last five (5) years, each with a value of at least USD 10,000,000 (United States Dollars ten million) that have been successfully and substantially completed. Substantial completion shall be based on 80% or more Plant and installation completed under the contract.
82 | Volume II. EMPLOYER’S REQUIREMENTS | ● 13.5 KM 33kV Evacuation line of OH Line circuit and an underground circuit complete with poles, conductors, insulators as per relevant standards. The 33kV evacuation line off takes power from the new PV power plant to the newly proposed Distribution substation. ● The newly proposed Distribution Substation comprising of 2No. 5/6.5MVA ONAN/ONAF of 33/11 kV ONAN type transformers complete with all its necessary protection schemes. | 1. This project includes two substations, one is photovoltaic area substation (PV Substation), the other is newly proposed Distribution substation (New Substation). And the two substations are connected via two 13.5km 33kV lines (OHL + UGL). Please confirm. 2. In the scope of work, the equipment of 11kV and below in New Substation is not mentioned. Our understanding is that in New Substation, the scope of work only includes the 33kV switchgear and the two 33/11kV transformers, and does not include the equipment of 11kV and below. Please clarify and specify the scope of work for the New Substation. | 1. The project includes two substations: one photovoltaic area substation (PV Substation) and a newly proposed Distribution substation (New Substation), with the two substations connected via two 13.5 km 33kV lines (OHL + UGL). 2. The scope of work for the New Substation includes the 33kV switchgear and the two 33/11kV transformers, but does not include the equipment for 11kV and below.
83 | 127 | 23. Supply of an extensible 33/36kV MV Switchgear (combiner panel for all Transformer bays and outgoing feeders) with 5No. Transformer Bay feeders, 2 outgoing feeders plus 4 No. spares complete with its power back up supply with Battery Chargers | These are two descriptions about the 33kV switchgear in the PV Substation which is inconsistent. Please clarify which one is correct. | No inconsistency at all. The additional numbers stand for spares. Refer to the SLD
84 | Volume-II | 33kV HT Synchronizing or combiner panel of an extensible type, rated a minimum of 1600A with a minimum of an incoming transformer feeder bays of 8No. 1250A VCB. The outgoing feeders shall be of a minimum of 4 No. each rated at 1250A VCB. The panel shall have a VCB breaker based on bus coupler of normally open type.
85 | Volume I | 24. 13.5 km 3Phase 33kV OH Line in 195 mm2 ACSR (Wolf) conductors, including, concrete poles, insulators, cross arms, stays, earthing, surges fittings, and any other fittings necessary for proper functioning of the system. 26. 13.5 km 3Phase 33kV UG Line of 3C 185 mm2 AL/XLPE/STA/PVC cable complete with all its protection equipment and devices system. | According to Volume I, there are two 33kV outgoing lines in this project; But in Volume II, the New Substation have 4 incoming feeder bays, Please clarify. | 2 are spares and 2 are to be supplied and excuted under this current scope
86 | volume II. | There is an extensible Supply& Installation of 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation.
87 |  |  | Please confirm if the project is to switch to islanded mode and work as a hybrid system or only on grid mode using PPC or MGC or both. This has major design implications for BESS -in grid forming & black start capability- and EMS | The project is designed to primarily operate in grid mode using the Power Plant Controller (PPC), with support for hybrid mode to coordinate the Battery Energy Storage System (BESS) and solar PV system. According to the General Technical Parameters (GTP) for the BESS, black start and grid-forming capabilities are required. The Master Controller plays a key role in managing this integration, ensuring optimal power distribution and grid As per the contract, the Master Controller is the Contractor’s responsibility, who must provide a suitable controller that meets the technical and operational specifications, along with required documentation and integration details
88
89 |  |  | The Single Line Diagram (SLD) listed in Appendix 1 is missing. Please provide the actual diagram illustrating the interconnection of PV, BESS, transformers, and 33kV evacuation line. | Refer to the SLD
90
91 |  |  | Site layout drawings are not included. Kindly provide layout drawings indicating equipment placement, cable routing, and site boundaries. S | Refer to the route diagam google earth drawings
92
93 |  |  | Clarification is needed on the exact Point of Interconnection (POI) for the 33kV line. Project gallery file JPG, JBEG, PDF OR GOOGLE DRIVE link if applicable | the exact point for the inteconnection will be the substation for the coordinates refer to the site diagrams
94
95 |  |  | Clrarification is needed on the exact transmission line rout. Please send GIS shapefiles / Google Earth (KML/KMZ) that indicating the geographical pole’s location. | Refer to the route diagram google earth drawings
96
97 |  |  | We request geotechnical, topographical, or soil condition data for the proposed site, off-site for transmission line to support foundation and structural design | Refer to the site asessment report , EHS and EIA Reports
98
99 |  |  | To proceed for the preliminary design, please providing us with the inception report, design criteria & design philosophy for the new integration requirement, grid code It is required the PVsyst and HOMER preliminary and visibility studies project reports | Employer has provided its own requirement in volume II under employer's requirement, therefore, its is the responsibility of the contractor to come up with a design and solution that could meet the provided requirement.
100
101 |  |  | Environmental and Social (ES) requirements mentioned available @ this link https://moem.govsomaliland.org/ unfortunately not working | the Environmental and Social (ES) report mentioned in the link will be forwarded along with other supporting documents for your reference
102
103 |  |  | Sub-Clause 9.3 of the General Conditions of Contract – permits & approvals Scope of Responsibility: Please confirm whether the Contractor is expected to obtain permits related to Grid interconnection, Land use and environmental approvals, Civil works and local construction permit | All permits, licenses and approvals are to be obtained by the contractor
104
105 |  |  | In Clause 4.9.8 is in inconsistency with the clause 4.9.8.2 Warranty. it is stated that the battery system’s End of Life (EOL) must be not less than 20 years from the date of commissioning. However, typical lithium-ion batteries reach EOL based on: • A threshold of 70% remaining capacity, as per warranty. • OR RTE during 15 years at POI. Kindly clarify: 1. Is the Contractor expected to design for 20 full years of calendar life regardless of cycles and degradation? 2. Will battery augmentation or replacement be allowed (and counted toward the 20-year requirement)? 3. Is the minimum retained capacity (e.g., 70%) at year 20 to be guaranteed? | 15-year performance guarantee ensures that the system maintains at least 70% SoH and RTE, and any necessary replacements or augmentations within that period are required and covered by the contractor. The 20-year design life is expected but not guaranteed under the same performance standards beyond 15 years
106
107 |  |  | There is an extensible Supply& Installation of 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation. please provide SLD | Refer to the SLD
108
109 |  |  | what does 90% PR mean for PV module, AC or DC? | 90% after the system DC losses
110
111 |  |  | Documentary evidence confirming that the Manufacturers’ is Tier 1with at least a minimum 10 years’ experience of manufacturing similar equipment.Documentary evidence shall include information of the factory locations. Do we have to provide for all the following | Yes, all equipment must be Tier 1, and documentary evidence confirming the manufacturer's Tier 1 status, at least 10 years of experience, and factory locations must be provided for all equipment.
112 |  |  | Do we have to provide all of the following?
113 |  |  | - Solar Photovoltaic Modules
114 |  |  | - PV Inverters
115 |  |  | - Battery Inverters
116 |  |  | - Batteries
117 |  |  | - Cables& Conductors
118 |  |  | - Power Transformers
119 |  |  | BESS and EMS
120 |  |  | - 33kV Synchronization/ combiner and Transformer MV Panels
121 |  | II. Technical Standards in Tender Documents,4.2 Photovoltaic Mounting Structures | Query: The design standards, civil materials, and geotechnical/seismic/concrete requirements are based on EN (Eurocodes) or ASTM (U.S. standards). As Chinese design institutes cannot implement these, may Chinese National Standards (GB) be substituted? | Yes, Chinese National Standards (GB) can be substituted, provided that they demonstrate equivalence in quality and performance to the EN (Eurocodes) or ASTM (U.S. standards) specified in the tender documents. The equipment or materials must meet the same standards of safety, reliability, and performance as those outlined in the Eurocodes or ASTM standards.
122 |  | The PV installation structures shall comply with the following standards or equivalents:
123 |  | EN 1325: Geotextiles and geotextile-related products - Characteristics required for earthworks, foundations, and retaining structures
124 | 124 | ISO 14713-1:2009: Guidelines for corrosion protection
EN ISO 1461: Hot-dip galvanized coatings
ISO 9223 & 9224: Corrosion of metals and alloys - Atmospheric corrosivity
EN 755-2:2008, Table 42: Mechanical properties
EN 573-3:2007, Table 06+: Chemical composition
ASTM B580-79: Anodic oxide coatings
ASTM A123: Standard specification for zinc (hot-dip galvanized) coatings on iron and steel products
ASTM A6: Standard specification for structural steel
EN 1990: Basis of structural design
EN 1991-1999: Eurocodes for structural actions and design (concrete, steel, composite, masonry, geotechnical, seismic, aluminum)
EN 206: Concrete specification, performance, production, and conformity
EN 12350: Testing fresh concrete
EN 12390: Testing hardened concrete
137 |  | Unless otherwise specified, all materials and services under this contract shall comply with the latest revisions of IEC or BS standards, applicable local standards, and material specifications. Suppliers not adhering to IEC/BSI standards may provide equipment meeting other recognized national standards, provided they demonstrate equivalence in quality and performance to IEC/BS standards and address any material deviations.
138 |  |  | What is the recommended quantity and configuration of string inverters and substations to ensure system redundancy and minimize downtime during equipment failures? | It’s the bidder to design which shall be approved by the employer
139 |  |  | Please confirm the percentage of spare parts required under PCC 7.3, which mandates the supply of spare parts for a period of two (2) years. | While the exact percentage of spare parts required is not provided in the bid document, it is clear that the contractor should maintain sufficient inventory for consumable spare parts and supply the necessary non-consumable spare parts as needed. The contract price will include the purchase price and all related costs (including the contractor’s fees), and the quantities and specifications of spare parts should be agreed upon with the employer
140 |  |  | 1. PoA for JV formation a) For a JV of three foreign entities, must the PoA be notarized in each entity's home country and legalized for Somaliland? b) Is a single PoA sufficient for the JV representative, or must each member submit one? | PoA for JV Formation: a) Shall be notarized from their country of origin b) A single PoA for the JV representative is sufficient, provided it authorizes the representative to act on behalf of all JV members
141 |  |  | ) JV Liability
142 |  |  | a) Will the JV be jointly and severally liable, or can liability be allocated among members? | Refer to ITB 4.1 and BDS 21.3(b) for details
143 |  |  | b) Given the JV limitation of three members, can you confirm whether sub-contractors' experience can supplement the JV's technical capacity? | Subcontrcators are not part of the JV arrangement,therefore their experience shall not be considired under evaluation. Its shall be considered only under specilaist works as a subcontractor not for general and specific experience.
144 |  |  | Considering the sheer volume of certain testing reports a) Can digital copies of certificates (ISO, test reports) be submitted initially, with hard copies later? b) For past projects, are LOAs and completion certificates sufficient, or are full contracts required? | a) Both hard copy and soft copy documents should match and be submitted at the same time b) For past projects, LOAs and completion certificates alone are insufficient. The required documents are Completion Certificates, Award Letters, signed contracts, and summary pages of the final accounts for each project, along with the contact personnel details.
145 |  |  | a) Are there any local content requirements affecting scoring? b) Are there milestones tied to payments? | a) Refer to ITB BDS 32.2 under evaluation of technical parts. B) Payment is a milestone based
146 |  |  | The Bidder may express the Bid price in any currency and the quotation currency must match the payment currency (the bid price is in USD). Therefore, all price can be in USD, and there is no need to consider local expenses in local currency. Please confirm. | All the payments/bid prices are USD as per the Bid. Please ITB 36.2
147 |  |  | Under CIP Incoterms, the buyer is responsible for import clearance and payment of import duties. Refer to Volume I, Page 118, Schedule of Rates and Prices Schedule No. 1 / No.2 / No. 3, Column Taxes & Duties, please elaborate on what TAXS & DUTIES include. | ll forms of taxes shall be borne and taken care by the contractor
148 |  |  | For proof of experiences stated in sub-factor 4.1, is filling the Form EXP 4.1 enough? If not, what kind of further documents should we provide? | Project Certificates: Official documents or completion certificates from previous clients that confirm the successful delivery and scope of past projects. Reference Letters: Letters from previous clients or partners that attest to your performance and the successful execution of relevant projects. Contract Copies: Copies of contracts for past projects that relate directly to the experience claimed. This can include scope of work, terms, and the role your company played.
149 |  |  | • For proof of experience stated in sub-factor 4.2(a), is filling the Form EXP 4.2(a) enough? If not, what kind of further documents should we provide? | Project Completion Certificates: These are official confirmations from clients or project owners that verify the completion of projects listed in the form, detailing the scope and your role. Reference Letters: Obtain letters from previous clients or stakeholders that provide feedback on your performance and the successful execution of projects that align with sub-factor 4.2(a). Contracts or Agreement Copies: Include portions of contracts that specify your responsibilities in previous projects, particularly those aspects that are pertinent to sub-factor 4.2(a).
150 |  |  | • For proof of experience stated in sub-factor 4.2(b), is filling the Form EXP 4.2(b) enough? If not, what kind of further documents should we provide? | Project Completion Certificates: These certificates should clearly state the installed capacities handled in the projects, verifying the scope and your successful role in achieving them. Contracts or Contract Excerpts: Provide specific sections from contracts that detail your responsibilities concerning installed capacities, underscoring your direct involvement and expertise in handling significant capacities. Reference Letters: Obtain letters from clients or project managers that specifically mention your effectiveness in managing and executing projects involving the stated capacities.
151 |  |  | Can we change the personnel in key personnel list before contract phase? | Changes to key personnel after bid submission require World Bank approval and must be justified by legitimate reasons such as health issues or employment changes. Replacement personnel should have qualifications that match or exceed those of the original candidates. Detailed justifications and transparent documentation of the qualifications of new personnel are necessary. World Bank Procurement Regulations document that pertain to the need for approval and management of changes in key personnel after bid submission are found in Section III.

## Sheet2
The plant is designed to operate for 25 years. The operation and maintenance (O&M) of the plant will be handled by the local Electricity Service Provider. However, for any repair works arising from project-related defects, the contractor is responsible for addressing these issues in accordance with the Defect Liability Period (DLP), as outlined in the contract terms.
Regarding the functional guarantee and plant performance, the contract clearly stipulates how these aspects will be handled, ensuring that any performance-related issues are managed according to the agreed-upon terms."
Answer to the Question (Incorporating the Table Information):
Based on the technical specifications of the Battery Energy Storage System (BESS) outlined in the table, and considering the IEC 62933-2-1 standard, here's a summary:
Charge-Discharge Efficiency: The System AC-DC-AC Efficiency is specified to be greater than 90%. This indicates the round-trip efficiency during the operation of the energy storage system, which is the ratio of energy discharged to energy charged, factoring in losses during the conversion processes. Therefore, the round-trip efficiency is evaluated according to >90% efficiency, as mentioned in the table.
Point of Connection (POC): The Point of Connection (POC) for this system is at 33kV, which is consistent with the grid integration for delivering power. The charge-discharge efficiency, as well as the BESS Availability, should be evaluated at the POC.
BESS Availability: The availability of the system, which includes both scheduled and unscheduled maintenance, is required to be about 95%. This aligns with the project reliability and operability requirements stated in the 4.9.8.1 section, where availability is based on system power capability at the POC.
Battery Technology and Capacity: The system should meet a minimum of 6000 cycles at rated energy capacity, with a minimum of 36 MWh nameplate capacity, and at least 34 MWh dispatchable at the beginning of life (BOL). The energy capacity should not be less than 70% of this capacity at any point of time up to the end of the battery life.
Summary Answer:
The charge-discharge round-trip efficiency of the BESS is evaluated to be greater than 90%, as specified in the technical requirements. The Point of Connection (POC) for this efficiency measurement is at 33 kV, which is the grid connection point for the system. According to the IEC 62933-2-1 standard, the efficiency test point is Point E.