## Sheet1
S.N. | Volume/Section | Clause No. | Bidder's Query | Employer's Clarification
Technical part
1 |  |  | Please provide the Topographic map and Geological Report of the whole plant. | Refer to the site assessment report
2 |  |  | Please provide KML files of PV power plants and transmission lines; | Refer to the SLD, and Transmission Route Diagram
3 |  |  | Please provide the SLG and electrical general layout of the opposite substation; | Refer to the SLD and the site diagram report
4 |  |  | Please provide geological survey, hydrology and meteorology documents of photovoltaic power plant; | Refer to the site assessment report
5 |  |  | Please provide APPENDIX 1: SLD FOR THE POWER PLANT in the technical bid; | Refer to the SLD of the project provided
6 |  |  | Please provide the Line route maps of the two outgoing transmission lines. | Refer to the route map of the transmission line
7 |  |  | Please provide the red - line drawing of the plant site area. | Refer to the site diagram
8 |  |  | Please clarify the size and scope of the 11kV substation on the opposite side | the scope of the bidder is up to the step down transformer 33/11 KV
9 | Volume-II | 3.1.1 Solar PV Power Plant General Scope Acceptable PR ratio for the PV system | 1. Please clarify where the evaluation point for 90% PV power generation efficiency is. Is it on the 33kV switchgear at the booster station or on the AC output side of the PV inverter? 2. If 90% PV power generation efficiency is evaluated on the 33kV switchgear at the booster station, there is no actual completed project to do this. Will efficiency below 90% be accepted? Is over-configuration accepted? | According to the IEC 62933-2-1 standard, metering must be conducted at the 33 kV switchgear of the booster station, including the consumption of auxiliary power within the energy storage system to ensure accurate performance evaluation. The project requires a charge-discharge round-trip efficiency (RTE) greater than 90%, and bids with lower efficiency are unlikely to be accepted. Evaluation will focus on the bid's performance guarantees and efficiency values to meet the project's standards or justifications for any deviations. The highest RTE values for PV BESS are typically achieved with modern lithium-ion systems, with the upper range generally between 90% and 95%, making them ideal for meeting the project’s RTE requirements.
10 | Volume-II | 4.9.3 Technical Specification of Battery Energy Storage System System AC-DC-ACEfficiency >90% | 1. Please clarify the location of the assessment point. 2. Whether the self-supply transformer is included; | the assessment point is the POC 33 KV, and all auxilary equibments are included
11 | Volume-II | 4.8.6 Circuit Breaker Technical Particulars Circuit Breaker Technical Particulars，40kA rms 3 sec for bus coupler，incomer and 31.5kA for bay module，31.5kA | Regarding the Rated short-circuit breaking current fo the 33kV system, the GTP shows 31.5kA/3s, but the bidding document shows 40kA rms 3 sec for bus coupler，incomer and 31.5kA for bay module.The bus coupler has a 31.5kA opening capacity, which is sufficient. Is it acceptable to have a 31.5kA opening capacity? | The Rated Short-Circuit Breaking Current of the 33kV GIS is likely 31.5 kA for 3 seconds, as indicated in both the GTP and the bidding document for the bay modules. The 40 kA for 3 seconds mentioned for the bus coupler/incomer applies to the main switchgear and not directly to the GIS, unless otherwise specified for the entire system.
12 | Volume-II | 13.1 TYPES OF WORKS 100mm layer of ballast aggregates to solar field platform | Please clarify whether it is installed in the entire photovoltaic plant or only in the maintenance channel
13 | Volume-II | 3.1.2 Solar PV Power Plant - Scope of Supply and Installations 33kV HT Synchronizing or combiner panel of an extensible type, rated a minimum of 1600A with a minimum of an incoming transformer feeder bays of 8No. 1250A VCB. The outgoing feeders shall be of a minimum of 4 No. each rated at 1250A VCB. The panel shall have a VCB breaker based on bus coupler of normally open type | Please clarify which one is correct | Please be advised that for all technical specifications related to the project or to the 33kV HT Synchronizing/Combiner Panel, the correct and final reference shall be Volume II – Employer’s Requirements
| Volume-I | Supply of an extensible 33/36kV MV Switchgear (combiner panel for all Transformer bays and outgoing feeders) with 5No. Transformer Bay feeders, 2 outgoing feeders plus 4 No.spares complete with its power back up supply with Battery Chargers
14 | Volume-I | Supply of an extensible 33/36KV MV Switchgear (combiner panel for all the incoming feeder bays) with 2No.line feeders, 2 outgoing feeders plus 2 No. spares complete with its power back up supply with Battery Chargers | Please clarify which one is correct | Please note that all specifications for the 33kV GIS Switchgear shall be as per Volume II – Employer’s Requirements,
| Volume-II | There is an extensible Supply& Installation of 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation
15 | Volume I | 24. 5 km 3Phase 33kV OH Line in 195 mm2 ACSR (Wolf) conductors, including, concrete poles, insulators, cross arms, stays, earthing, surges fittings, and any other fittings necessary for proper functioning of the system. 26. 5 km 3Phase 33kV UG Line of 3C 185 mm2 AL/XLPE/STA/PVC cable complete with all its protection equipment and devices system. | According to Volume I, there are two 33kV outgoing lines in this project; But in Volume II, the New Substation have 4 incoming feeder bays, Please clarify. | Please note that all specifications for the 33kV Overhead and Underground Lines shall be as per Volume II – Employer’s Requirements, Section 3.1.2, which defines the supply and installation of 33kV GIS switchgear with 4 No. incoming feeder bays (2 for OHL and 2 for UG lines). Any differing details in Volume I are to be disregarded.
| volume II. | 3.1.2 Solar PV Power Plant - Scope of Supply and Installations There is an extensible Supply& Installation of 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation.
Financial part
1 | Volume I | Various duties, levies and Taxes shall be borne by the contractor | Please clarify except customs and import duties what's other duties need be borne by the contractor | The contractor is responsible to identify all duty requirements
2 | Volume I | The Bid shall be valid until: To be updated unpon approval | plsease clarify the bid valid day | minimum 120 days after the submission of the bid. Which is 12-October 2025
3 | Volume I | Installation Services shall be quoted separately (Schedule No. 4) and shall include rates or prices for local transportation to named place of final destination as specified in the BDS, insurance and other services incidental to delivery of the Plant, all labor, contractor’s equipment, temporary works, materials, consumables and all matters and things of whatsoever nature, including operations and maintenance services, the provision of operations and maintenance manuals, training, etc | plsease clarify how many years need contractor quoted for operations and maintenance services | 3 years of preventive maintenance is required after the period of defetc liability
4 | Volume I | Bidder’s audited Financial Statements for the last eight (8) years as stipulated in Section III of the Evaluation criteria. | plsease clarify 8 years or 5 years audited Financial Statements need be provied by contractor | The contractor is required to provide the financial statements of 5 years , (2019 - 2024)
| Volume I | Submission of audited balance sheets or if not required by the law of the Bidder’s Country, other financial statements acceptable to the Employer, for the last five (5) years (2019-2023) to demonstrate the current soundness of the Bidders financial position and its prospective long term profitability
5 | Volume I | The bidder should have an experience in Design, Supply, Installations, Testing and Commissioning for the PV Power Plant with an integration of BESS and Diesel Gensets. The bidder shall demonstrate to have carried out atleast Three (3No.) projects which are completed with a minimum capacity of 10 MWp PV with Battery Storage Capacity each. The projects shall have been carried out in the last ten (10) years and shall have been in satisfactory operation Six (6) months before the submission date. Completion Certificates, Award letters, signed contracts and summary pages of the final accounts shall be submitted for each together with the details of the contact personnel. | The requirement for Bidder to submit the specific experience is inconsistent between BDS and Evaluation Criteria, please clarify which requirement shall be followed. Meanwhile, the description for Substantial completion is 80% or more Plant and installation completed under the contract in Evaluation criteria. But in BDS, it is required the completed project experience, please please clarify which requirement shall be followed. | both requirement shall be followed as they are related to two different evaluation criterias 4.2 (a) which is related to the financial capability and the bidder is required to submit three contracts within the last 5 years where each one is $10,million USD, that have been successfully and substantially completed and 4.2 (b) is related in terms system capacity and the bidder is required to provide three completed projects with a cpacity of 10 MW PV with BESS implemented within the last 10 years and have been in satisfactory operation Six (6) months before the submission date
| Volume I | (a) Participation as contractor, joint venture member, or subcontractor, in at least three (3) contracts within the last five (5) years, each with a value of at least USD 10,000,000 (United States Dollars ten million) that have been successfully and substantially5completed and that are similar to the proposed Plant and Installation Services. relevant Cyber security accreditation such as ISO 27000 (ISO 27001) or equivalent. Substantial completion shall be based on 80% or more Plant and installation completed under the contract.
5 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.1.2) Solar PV Power Plant - Scope of Supply and Installations 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation. . | Please clarify which outgoing feeders of the 33 kV HT panel are designated for Overhead Lines (OHL) and which are for Underground (UG) cables, or if any outgoing feeder can be used for either type depending on termination arrangements. | There are no fixed layout restrictions tying any outgoing feeder to OHL or UG use. The feeder type is flexible and depends only on the termination arrangements and protection configuration
1 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.0) PROJECT SPECIFIC DATA Project Coordinates： Latitude: 9°56'11.80"N Longitude: 43° 8'53.16"E | Please provide accurate boundary coordinates and occupation drawings for the Solar PV Power Plant | the boundary coordinates are provided in the bid document, moreover further informationof the site will be provided in the in the site assessment report
2 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.1.1) Solar PV Power Plant General Scope Acceptable PR ratio for the PV system 90% | Actual operational PR under real site conditions, as industry-standard PR typically ranges from 82% to 85%. | the required Performace Ratio of the system is 90%. Which reflects the quality and the efficiency of the system
3 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.1.2) Solar PV Power Plant - Scope of Supply and Installations - 13.5 KM 33kV Evacuation line of OH Line circuit and an underground circuit complete with poles, conductors, insulators as per relevant standards. In Subject Title - System including 5 km of 33kV Evacuation line for Awdal Electric Company (AEC): Borama, Somaliland. | The two clauses conflict with each other. Please confirm correct line distance for evacuation (5 kM or 13 kM) & provide route diagram of evacuation line. | the provided requirement of the evacuation line is 5km
4 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.1.2) Solar PV Power Plant - Scope of Supply and Installations The newly proposed Distribution Substation comprising of 2No. 5/6.5MVA ONAN/ONAF of 33/11 kV ONAN type transformers complete with all its necessary protection schemes. | Please provide detailed boundary coordinates and land occupation drawings for the proposed Distribution Substation | will be included in the site assessment report and the route diagram
5 | VOLUME II. EMPLOYER’S REQUIREMENTS | (3.1.2) Solar PV Power Plant - Scope of Supply and Installations 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation. . | Please clarify which outgoing feeders of the 33 kV HT panel are designated for Overhead Lines (OHL) and which are for Underground (UG) cables, or if any outgoing feeder can be used for either type depending on termination arrangements. | There are no fixed layout restrictions tying any outgoing feeder to OHL or UG use. The feeder type is flexible and depends only on the termination arrangements and protection configuration
6 | VOLUME II. EMPLOYER’S REQUIREMENTS | 15. APPENDICES APPENDIX 1: SLD FOR THE POWER PLANT. | The Single Line Diagram (SLD) listed in Appendix 1 is missing. Please provide the actual diagram illustrating the interconnection of PV, BESS, transformers, 33kV evacuation line & electrical general layout of the substation. | the SLD will be provided along with the other supportive documents
7 | VOLUME II. EMPLOYER’S REQUIREMENTS | 4.1.2 WARRANTIES FOR MODULES - 4.1.2.2 Performance Warranty In the case of string Inverters, average voltage drops (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. | Regarding the calculation of the influence of cable operating temperature on cable resistance, the requirement of 0.5% average voltage drop for DC cables is too high. Currently, it is impossible to truly achieve this requirement in global implementation projects. Is it acceptable to adopt the common voltage drop requirements of 1.5% or 1% in current global projects? | the average voltage drop from the PV modules to the string inverter must be limited to 0.5% of the rated voltage. While achieving this is feasible, it depends on selecting appropriately sized cables based on distance and current load. If a 0.5% voltage drop cannot be met, the Contractor must submit detailed voltage drop calculations in an Excel sheet. In such cases, a voltage drop of up to 1% may be considered acceptable.
8 | VOLUME II. EMPLOYER’S REQUIREMENTS | 4.9.3 Technical Specification of Battery Energy Storage System BESS System AC-DC-ACEfficiency ＞90% | Does 90% efficiency include auxiliary load consumption within the energy storage system? | since the efficiency is measured according to the IEC 62933-2-1 standard at the 33 kV switchgear, the auxiliary load consumption shall be accounted for, ensuring a comprehensive evaluation of the system's overall performance
3 | VOLUME I. SECTION III , EVALUATION AND QUALIFICATION CRITERIA | Submission of Auodited balance sheets or if not required by the law of the Bidder’s Country, other financial statements acceptable to the Employer, for the last five (5)years (2019-2023) to demonstrate the current soundness of the Bidders financial position and its prospective long- term profitability. | Is it ok if balance sheet is in french lunguage? | As per ITB 10.1, all bids, correspondence, and supporting documents must be in English. Documents in other languages, must be accompanied by a certified English translation from a reputable firm.
| Volume II |  | In this list on volume 2 for GTPs- item e) PCU(Power Conditioning Unit) is not present | in the GTP form the string inverter requirement specifications are provided, similary the BESS technical requirements are provided, the bidder is required to bring PCU which can allign with the requirements of the BESS, or similarly the specification requirements of the string inverter can be considered.
|  |  | 1. Please confirm whether the following document is the final version of the bidding document. Many dates, such as the bid submission deadline and the bid validity period, have not been filled in. AEC_RFB_Volume-I_08.04.25_Final Final 13042025(1).docx RFB AEC -Volume-II ver 2- 02-18-25 final 13042025.docx | Please try to get the RFB documents in the webpage of the ministry or the adevertised links as they are the final version with all details. Following are the links you can access a) https://moem.govsomaliland.org/ . B) https://docs.google.com/forms/d/e/1FAIpQLSdxkIB5ujMCBaU0k4ejH9_rSQwGDV0HgURh2-Rl8Z71ePJHHw/viewform
|  | The Bidder shall check the dimensions of rooms and outdoor plots where electrical equipment is proposed to be erected. The rooms and plots must accommodate the equipment as well as having workspace for operators and maintenance personnel. | Could you please indicate where is the location (PV field area) to install the PV module and relevant equipment, such as transformer, PV inverter and BESS containers. | Refer to the site diagram
|  | The civil and structural works to be constructed under this Contract include the following: -Work for access and Power plant internal roads. The contractor shall be responsible for designs of all the civil and structural components and implementation of approved designs for the civil-related works that falls within its scope. | Could you please clarify who will take the job to build the access road and internal road? As well as the power house, control rooms. | The local utility provider will manage site preparation, while the contractor will handle the civil and structural work for the PV power plant's installation and commissioning, including internal access roads within the plant
|  |  | The border shared from the employer is departed 2 parts, is it possible to dismantle the existing fence which in the center please? Also, the existing PV arrays are not installed at true North-South direction, would you please indicate the installation direction of the new PV arrays? Shall we follow the existing PV arrays or true North-South mentioned in the tender book? | Yes, the bidder can dismantle the existing fence in the center, provided the employer agrees to it.Regarding the installation direction of the new PV arrays, it will depend on the design of the contractor. There is no requirement to follow the direction of the existing PV modules
|  |  | How long is the project duration? | the maximum duration allocated for the project is 15 months
|  |  | When will the project start? | The project will start as soon as the successful bidder is selected and the contract is signed
|  |  | Is the bid evaluation based on scoring or the lowest price? | The bid evaluation is based on a quality and cost-based approach. The following weightings shall apply:Rated Criteria (including technical and non-price factors): 80% and Bid Cost: 20%
|  |  | What is the composition ratio of the construction personnel? | The composition ratio of the construction personnel is not fixed but must meet the project’s specific requirements. The Bidder must demonstrate that it will have a suitably qualified Contractor’s Representative and other suitably qualified key personnel, in adequate numbers, as described in the Employer’s Requirements.
|  |  | What percentage of local employees is required? | The percentage of the local employees is not fied but The Contractor is encouraged to use local labor that has the necessary skills
|  |  | Is the power transmission distance confirmed to be 5 kilometers or possibly longer? Is it necessary to carry out access transformation at the grid connection point? Are all these costs included in the bidding price? | there are two routes one is 5.3 kM and the other one is 6.5 kM refer to the kmz route diagrams
|  |  | there is no place to fill in taxes and duties in the BOQ form, does this mean that bidders do not need to pay taxes and duties, and the total price does not need to take taxes and duties into account, please clarify. | Accoridng to PCC Clause 14.2 (a) & (b) – Taxes and Duties: Various duties, levies and taxes shall be borne by the Contractor.Even though taxes and duties are not itemized separately in the BOQ, bidders must include them in the CIP unit prices
|  |  | Can you please explain about taxes and duties on imported items | Refer to PCC 14.2 (a) & (b) Taxes & Duties, Various duties, levies and Taxes that shall be borne by the contractor.
|  |  | Given the potential poor port and road infrastructure in the region, could this lead to delays or damage during equipment transportation | Delay in completion will incur penalty charges.
|  |  | What is the payment condition? Suppliers need to make sure payment is received before FOB release Please specify the payment timeline? | In accordance with GCC Clause 12 (Terms of Payment), the Employer shall pay the Contractor based on the Price Breakdown in the Price Schedules.
|  |  | In case of JV, do all the JV Partners need to sign all the documents ? | In a JV, all partners must sign the documents unless one is authorized to sign on behalf of the others through a valid Power of Attorney.
|  |  | Does the contractor have any obligation in terms of reporting towards the PIU? | Yes, the contractor has an obligation to report to the project manager and the PIU. Regular reporting is typically required on progress, quality, issues, and compliance, as outlined in the contract and the Employer’s Requirements.
|  |  | is the medium voltage under ground cabling coming from another location other than the Solar Plant sub station | No
|  |  | It is written that DAS & communication infrastructure to transfer the real time data to load control centers. Please clarify the load control centers (is it the 33/11KV new Substation or the RLDC?) | The load control centers for receiving real-time data from the BESS via DAS are the Regional Load Dispatch Center (RLDC)
|  |  | Defect Liability period of project is 12 months or 18 months? | the defect liability is 1 year from the date of Operational Acceptance,
|  |  | In case the bidder proposes to form a Joint Venture (JV) after the award of the contract, would a Letter of Intent to form the JV be considered sufficient for the purpose of bid submission along with the draft JV agreement | letter of intent and JV agreement is sufficienct for the bid subimission
|  | "There is an extensible supply and installation of 1600 A, 33 kV GIS switchgear with a minimum of four incoming feeder bays (2 for overhead lines and 2 for underground lines), along with an outgoing feeder to the transformers for voltage transformation, which shall be located in the new substation." | Based on this, could you please clarify whether this means: • A total of four termination points at the GIS and two transmission lines ( OH& UG), or • Two transmission lines with two termination points, and the remaining two bays intended as spares? | A total of four termination points are required at the GIS switchgear: two for overhead lines (OH) and two for underground lines (UG).
|  |  | Please explain the general wiring logic among items 23 to 27 in bidding forms-Schedule of Rates and Prices-Schedule No. 1: Plant and Mandatory Spare Parts Supplied from Abroad? | The project requires the supply and installation of extensible 33kV switchgear systems rated at 1600A, serving both the solar PV plant and the substation. This includes a synchronizing/combiner panel at the PV site with 8 incoming transformer feeders and 4 outgoing feeders, all using 1250A VCBs. Additionally, a 33kV GIS switchgear is needed at the substation, featuring 4 incoming bays (2 for overhead lines and 2 for underground cables) and 2 outgoing bays to the 33/11kV transformers.
|  |  | Is the 33kV/11kV substation located close to the BESS, or is the BESS coupled with the PV system and then connected to the substation via a transmission line 5 km away? | The BESS coupled with the PV system and then connected to the substation via a transmission line
|  |  | For item 23 in bidding forms-Schedule of Rates and Prices-Schedule No. 1: Plant and Mandatory Spare Parts Supplied from Abroad, which includes 2 outgoing feeders plus 4 spares, are the two outgoing feeders intended for the 33kV underground line and 33kV overhead line mentioned in items 24 and 26? Or are they 11kV line feeders? What about the 4 Spares? | item 23 in the bid form is the 33kV GIS switchgear which is needed at the substation, featuring 4 incoming bays (2 for overhead lines and 2 for underground cables) and 2 outgoing bays to the 33/11kV transformers.
|  |  | A site layout plan are required, showing the site location, availability of space, 33kV line route and the PV plant, BESS plant, substation plant. Etc. | Refer to the route map of the transmission line
|  |  | Clarify the application type: off‑grid or grid‑tied? Whether to allow the grid to charge BESS? | The BESS is a grid-tied system with grid-forming capabilities for peak management, where charging from the grid is not allowed; it must be charged exclusively from the solar PV
|  |  | Clarify the current load situation and any future additional load requirements (should include the load curve and main load list, if available) | Refer to the load profile provided
|  |  | Confirm whether a diesel generator needs to be included in the system. | there is no diesel generator to be included in the project, but the curently exisiting diesel generators will be integrating into the new plant
|  |  | In Volume 1, ITB 11.2, the contractor is required to submit preliminary designs, including calculations, system sizing, spare capacity, projected system losses, etc. These should also cover all fault analyses and the system's response under both steady-state and transient conditions. Such calculations require grid model parameters for simulation. to carry out the simulations, the necessary parameters need to be provided. | the load profile to be based on the design is provided
|  |  | In Volume II, clause 4.9.3 (Technical Specification of Battery Energy Storage System) specifies an energy rating of minimum 20 MWh nameplate capacity with at least 19 MWh dispatchable at the beginning of life, and a BESS availability of 95%. However, in Appendix 8 (Functional Guarantees), the requirements are 20 MWh capacity and 98% availability for the BESS. Which specification takes precedence? | In the case of conflicting specifications between different parts of the tender documents such as Volume II, Clause 4.9.3 and Appendix 8 (Functional Guarantees) the Functional Guarantees in Appendix 8 generally take precedence and shall be complied
|  |  | Are there any tall trees or mountain peaks obstructing the area around the photovoltaic power plant? | the employer will clear all the obstructions if there are any at the plant station
|  |  | In Volume II, APPENDIX 3: Guaranteed Technical Particulars-C.GTP for BESS, is the requirement that the container weight be less than 30 tonnes mandatory? | The requirement stated in the GTP for BESS is mandatory and the container's wheight must be less than 30 tons
|  |  | In Volume 1, Section X-Contract Forms-Functional Guarantees 3.1, the BESS round trip efficiency (RTE) requirement is difficult to achieve with current energy storage systems. Can this parameter requirement be reduced? | it can’t be reduced and shall be complied as its
|  |  | In Volume 1, PCC 12. Terms of Payment, the definition of the payment terms is stated as "Not Applicable". However, in Contract forms Appendix 1-Terms and Procedures of Payment, the specific payment method is clearly stipulated. What are the exact payment terms? | Refer to article 2 of the contract, and Appendix 1
|  |  | . In Volume 1, Schedule No. 2 in the Bidding Forms- Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country-is it acceptable to use USD as the currency? | yes
| Vol I | ITB 19.1 – Bid Validity Period: | The document states, “the bid shall be valid until: to be updated upon approval.” Could you confirm whether an explicit expiry date for submitted bids has now been established? | As per the officially published Specific Procurement Notice (SPN), the bid submission deadline is confirmed as June 14, 2025, at 9:30 AM Hargeisa Local Time
|  | ITB 23.1 – Bid Submission Deadline: | The deadline is indicated as “date: to be updated upon approval at 9:30 AM Hargeisa Local Time.” Please advise if a definitive submission deadline is currently available | Accordingly, the bid validity period shall be 120 days from the submission date, making the bids valid until October 12, 2025.

## Sheet3
The Bidder shall check the dimensions of rooms and outdoor plots where electrical equipment is proposed to be erected. The rooms and plots must accommodate the equipment as well as having workspace for operators and maintenance personnel. | Could you please indicate where is the location (PV field area) to install the PV module and relevant equipment, such as transformer, PV inverter and BESS containers.
The Bidder shall in his bid present arrangement drawings showing how he intends to adapt the equipment to the space available. If the space is not sufficient the Bidder shall indicate necessary enlargements. Failing to do so the Bidder shall bear the cost of later modifications of the facilities.
Note: Civil related works for offices, control rooms, perimeter wall, access roads for the site and within the site, site clearance shall be done by the local utility Service Provider which is the company planned to run the plant upon completion. The rest of the civil and structural work related for the proper erection, installation, testing and commissioning of the PV power plant shall be in the scope of the contractor. | Could you please clarify who will take the job to build the access road and internal road? As well as the power house, control rooms.
The civil and structural works to be constructed under this Contract include the following: -Work for access and Power plant internal roads. The contractor shall be responsible for designs of all the civil and structural components and implementation of approved designs for the civil-related works that falls within its scope.
• 13.5 KM 33kV Evacuation line of OH Line circuit and an underground circuit complete with poles, conductors, insulators as per relevant standards. The 33kV evacuation line off takes power from the new PV power plant to the newly proposed Distribution substation. | It seems same contents to the project Berbera, would you please share us the over head line route from the PV Plant Borama to the "newly proposed Distribution substation."
• The newly proposed Distribution Substation comprising of 2No. 5/6.5MVA ONAN/ONAF of 33/11 kV ONAN type transformers complete with all its necessary protection schemes. | Also, we sincerely request for the SLD and asociated drawings.
• There is an extensible Supply& Installation of 1600 A 33kV GIS switchgear with a minimum incoming feeder bay of 4No. (2 No. for OHL and other 2No. for the UG lines) with an ongoing feeder to the transformers for voltage transformation which shall be located in the new substation.
The border shared from the employer is departed 2 parts, is it possible to dismantle the existing fence which in the center please? Also, the existing PV arrays are not installed at true North-South direction, would you please indicate the installation direction of the new PV arrays? Shall we follow the existing PV arrays or true North-South mentioned in the tend

## Sheet2
The plant is designed to operate for 25 years. The operation and maintenance (O&M) of the plant will be handled by the local Electricity Service Provider. However, for any repair works arising from project-related defects, the contractor is responsible for addressing these issues in accordance with the Defect Liability Period (DLP), as outlined in the contract terms.
Regarding the functional guarantee and plant performance, the contract clearly stipulates how these aspects will be handled, ensuring that any performance-related issues are managed according to the agreed-upon terms."
Answer to the Question (Incorporating the Table Information):
Based on the technical specifications of the Battery Energy Storage System (BESS) outlined in the table, and considering the IEC 62933-2-1 standard, here's a summary:
Charge-Discharge Efficiency: The System AC-DC-AC Efficiency is specified to be greater than 90%. This indicates the round-trip efficiency during the operation of the energy storage system, which is the ratio of energy discharged to energy charged, factoring in losses during the conversion processes. Therefore, the round-trip efficiency is evaluated according to >90% efficiency, as mentioned in the table.
Point of Connection (POC): The Point of Connection (POC) for this system is at 33kV, which is consistent with the grid integration for delivering power. The charge-discharge efficiency, as well as the BESS Availability, should be evaluated at the POC.
BESS Availability: The availability of the system, which includes both scheduled and unscheduled maintenance, is required to be about 95%. This aligns with the project reliability and operability requirements stated in the 4.9.8.1 section, where availability is based on system power capability at the POC.
Battery Technology and Capacity: The system should meet a minimum of 6000 cycles at rated energy capacity, with a minimum of 36 MWh nameplate capacity, and at least 34 MWh dispatchable at the beginning of life (BOL). The energy capacity should not be less than 70% of this capacity at any point of time up to the end of the battery life.
Summary Answer:
The charge-discharge round-trip efficiency of the BESS is evaluated to be greater than 90%, as specified in the technical requirements. The Point of Connection (POC) for this efficiency measurement is at 33 kV, which is the grid connection point for the system. According to the IEC 62933-2-1 standard, the efficiency test point is Point E.